## How to use
12/12/19 v0.3 |  |  | Module B6 Operational Energy Datasheet - Guidance for Use
This datasheet contains information useful for energy modelling of office and residential buildings. Please note that defaults required for energy modelling for a Green Star assessment may differ from values provided here. Therefore if the
purpose of energy modelling is focussed on obtaining a Green Star assessment, it is advisable to contact NZGBC in order to obtain operational energy defaults for this purpose.
This datasheet is divided into the following worksheets:
|  | Occupancy by building activity: | Table B6:01 BUILDING OCCUPANCY PATTERNS
|  | Internal energy end uses: | Table B6.02a: TYPICAL SCHEDULE OF OPERATION
Table B6.02b HIGH SCHEDULE OF OPERATION
Table B6.02c LOW SCHEDULE OF OPERATION
|  | Internal heat gains | Table B6.03: PEOPLE HEAT GAIN MODELLING
Table B6.04: INTERIOR LIGHTING HEAT GAIN MODELLING
Table B6.05: HEAT GAIN TYPE & FRACTION ASSUMPTION FOR ALL ZONE ACTIVITIES
Table B6.06: ELECTRIC EQUIPMENT: HOT WATER GAIN
Table B6.07: ELECTRIC EQUIPMENT CONSUMPTION: PLUG LOAD HEAT GAIN MODELLING
Table B6.08: PEOPLE HEAT GAIN MODELLING: Residential
Table B6.09: INTERIOR LIGHTING ENERGY AND HEAT GAIN MODELLING: Residential
Table B6.10: ELECTRIC EQUIPMENT CONSUMPTION: PLUG LOAD ENERGY & HEAT GAIN MODELLING: Residential
Table B6.11: HOT WATER HEAT GAIN (FOR SPACE HEATING & COOLING LOAD CALCULATION) MODELLING: Residential
Table B6.12: OT WATER HEAT GAIN (FOR SPACE HEATING & COOLING LOAD CALCULATION) MODELLING: Residential
|  | Zone airflow & ventilation | Table B6.13: ZONE INFILTRATION: WHOLE BUILDING AVERAGE
Table B6.14: ZONE VENTILATION: OUTDOOR AIR REQUIREMENTS
Table B6.15: HVAC SCHEDULE OF OPERATION
Table B6.16a: RESIDENTIAL ZONE INFILTRATION
Table B6.16b: RESIDENTIAL ZONE VENTILATION: OPENING MODULATION
Table B6.16c: RESIDENTIAL HYBRID VENTILATION: CONDITIONS FOR OPENING WINDOWS/DOORS
|  | Thermostat setpoint & HVAC | Table B6.17a: THERMOSTAT SETPOINTS
Table B6.17b: TYPES OF HVAC SYSTEMS
Table B6.17c: RESIDENTIAL HEAT PUMP SETTINGS
|  | Building materials | Table B6.18: BUILDING MATERIALS
Table B6.19: ROUGHNESS (ENERGYPLUS)
|  | Air gaps | Table B6.20a: AIR GAP SPACE - MATERIAL AIR GAP WITH EFFECTIVE EMITTANCE (E) OF 0.82 & TEMPERATURE DIFFERENCE OF 12ºC
Table B6.20b: AIR GAP SPACE - MATERIAL AIR GAP WITH EFFECTIVE EMITTANCE (E) OF 0.5 & TEMPERATURE DIFFERENCE OF 12ºC
|  | Glazing & frames | Table 6.21: GLAZING MATERIALS
Table 6.22: GLAZING FRAME MATERIALS
Table 6.23: GLAZING FRAME MATERIALS
Values used for modelling energy for the reference buildings in LCAQuick are in black. Other values which have been found, but not used, are in grey and presented for completeness.
In order to calculate the environmental impacts of electricity use in buildings, use of the NZ grid electricity datasets available on the BRANZ website are recommended for consistency.
INTRODUCTION
The international standard ISO 21931-1 divides the building life cycle into stages, these being:
Processes prior to handover (Product Stage + Construction Process Stage) – including raw material supply, transport and manufacture of products up to the manufacturers’ gates and the construction process, including transport to the building site and installation or construction.
Processes during occupation (Use Stage) – including installed products in use, maintenance, repair, replacement and refurbishment and operation of the building, including building related energy use, water supply, use and wastewater treatment.
Processes following occupation (End of Life Stage) – including deconstruction, transport, recycling and disposal.
The European standard EN 15978 considers the building life cycle in the same way as ISO 21931-1, and provides numbered stages (or modules) illustrated below. It additionally includes (optional) Module D covering benefits and loads beyond the system boundary.
Typical (
EN 15978 allows use of "scenarios" to describe stages of the life cycle, where a scenario is defined as a "collection of assumptions and information concerning an expected sequence of possible future events". These must be described and documented, making clear any assumptions used.
This datasheet contains information to support Module B6 for use when conducting a Life Cycle Assessment of buildings. It may also be used in other applications, for example, to inform results published in "cradle to gate Environmental Product Declarations (EPD) with options". Data presented in this worksheet is intended to assist with filling data gaps and help to ensure that building LCAs are more consistent.
The information in this datasheet is based on a review of literature and other sources of data. Sources of information that have been used are cited.
Information about the methods used to develop this datasheet are provided in the BRANZ SR351 study report, which can be freely downloaded from the BRANZ website (www.branz.co.nz).
GUIDE

## Occupancy by Building Activity
12/12/19 v0.3 |  | Module B6 Operational Energy - occupancy by building activity
The table below sets out building activity occupancy patterns, and references from which these are drawn
Table B6:01 BUILDING OCCUPANCY PATTERNS
Notes
*1 BEES templates http://www.branz.co.nz/cms_display.php?sn=158&st=1&pg=9697
*2 Table C2 (Standards New Zealand, 2007a)
*3 User assumption based on local gym's actual opening hours
*4 NZS 4218:2009 Table G2 Housing. Assumed number of occupants is based on 1 person per bedroom + 1
*5 Occupanacy is evenly distributed based on zone area so the sum of the building's total occupancy for all zone does not exceed NZS 4218:2009 Table G2 Housing. An occupied area/space/zone is defined a space inhabbited not less than 15min e.g. Living rooms, kitchens (Clause 2.3, ASHRAE Standard 55-2004 Thermal Environmental Conditions for Human Occupancy) *5
| Office *1 | Retail *1 | Gym *3 | Restaurant *2 | Residential: Occupancy (building total, sum of all zones) *4 | Residential: Occupied Area Bedroom *5 | Residential: Occupied areas
| Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction
| Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31
| For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: WeekDays | For: WeekDays
| Until: 08:00 | Until: 09:00 | Until: 05:30 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00
| 0 | 0 | 0 | 0 | 1 | 1 | 0
| Until: 18:00 | Until: 20:00 | Until: 22:00 | Until: 11:00 | Until: 11:00 | Until: 11:00 | Until: 11:00
| 1 | 1 | 1 | 0.05 | 0.6 | 0 | 1
| Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00
| 0 | 0 | 0 | 0.5 | 0.6 | 0 | 1
| For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00
| Until: 24:00 | Until: 10:00 | Until: 07:00 | 0.8 | 1 | 0 | 1
| 0 | 0 | 0 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00
|  | Until: 20:00 | Until: 19:00 | 0.35 | 1 | 1 | 0
|  | 1 | 1 | For: Saturday | For: Saturday | For: Weekends | For: Weekends
|  | Until: 24:00 | Until: 24:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00
|  | 0 | 0 | 0 | 1 | 1 | 0
|  |  |  | Until: 11:00 | Until: 11:00 | Until: 11:00 | Until: 11:00
|  |  |  | 0 | 1 | 0 | 1
|  |  |  | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00
|  |  |  | 0.45 | 0.5 | 0 | 1
|  |  |  | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00
|  |  |  | 0.7 | 0.7 | 0 | 1
|  |  |  | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00
|  |  |  | 0.55 | 1 | 1 | 0
|  |  |  | For: Sunday | For: Sunday | For: AllOtherDays | For: AllOtherDays
|  |  |  | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00
|  |  |  | 0 | 1 | 1 | 0
|  |  |  | Until: 11:00 | Until: 11:00 | Until: 11:00 | Until: 11:00
|  |  |  | 0 | 1 | 0 | 1
|  |  |  | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00
|  |  |  | 0.2 | 0.5 | 0 | 1
|  |  |  | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00
|  |  |  | 0.55 | 0.7 | 0 | 1
|  |  |  | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00
|  |  |  | 0.2 | 1 | 1 | 0

## Internal energy end uses
12/12/19 v0.3 |  | Module B6 Operational Energy - internal energy end uses
Below is provided a typical schedule of operation for calculating internal energy end-uses, and to its right, high and low schedules of operation. The calculation of internal heat gains as a result of these energy end-uses is calculated using values listed in the Internal Heat Gains worksheet.
Use of Typical values is recommended in the absence of information that indicates use of high or low values is more appropriate.
| Table B6.02a: TYPICAL SCHEDULE OF OPERATION: Commercial/Retail | [7 empty] | Table B6.02b HIGH SCHEDULE OF OPERATION: Commercial/Retail | [5 empty] | Table B6.02c LOW SCHEDULE OF OPERATION: Commercial/Retail | [5 empty] | Table B6.02d SCHEDULE OF OPERATION: Residential
Reference
*1 BEES templates http://www.branz.co.nz/cms_display.php?sn=158&st=1&pg=9697
*2 Table C2 (Standards New Zealand, 2007a)
*3 User modelling assumption
| Typical Office Equipment Operation *1 | Typical Office Hot Water Operation *1 | Typical Office Lighting Operation *1 | Typical Retail Equipment Operation *1 | Typical Retail Hot Water Operation *1 | Typical Retail Lighting Operation *1 | Typical Restaurant Equipment / Lighting Operation *2 | Typical Gym Equipment / Lighting Operation *3 | High Office Equipment Operation | High Office Hot Water Operation | High Office Lighting Operation | High Retail Equipment Operation | High Retail Hot Water Operation | High Retail Lighting Operation | Low Office Equipment Operation | Low Office Hot Water Operation | Low Office Lighting Operation | Low Retail Equipment Operation | Low Retail Hot Water Operation | Low Retail Lighting Operation | Plug Load Equipment Operation Schedule: Source: NZS 4218:2009 Table G2 Housing
| Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction | Fraction
| Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31 | Through: 12/31
| For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: Weekdays | For: AllDays
| Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 08:00 | Until: 05:30 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 08:00
| 0.35 | 0.09 | 0.05 | 0.39 | 0.01 | 0.1 | 0.15 | 0 | 0.61 | 0.24 | 0.16 | 0.72 | 0.18 | 0.47 | 0.12 | 0.01 | 0.01 | 0.07 | 0 | 0.01 | 0.03
| Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 11:00 | Until: 22:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 11:00
| 0.34 | 0.06 | 0.04 | 0.37 | 0.01 | 0.06 | 0.4 | 1 | 0.59 | 0.21 | 0.18 | 0.74 | 0.31 | 0.51 | 0.12 | 0 | 0.01 | 0.07 | 0 | 0.01 | 0.23
| Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 18:00 | Until: 24:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 18:00
| 0.37 | 0.09 | 0.06 | 0.42 | 0.03 | 0.11 | 0.9 | 0 | 0.64 | 0.2 | 0.52 | 0.82 | 0.45 | 0.69 | 0.13 | 0.01 | 0.01 | 0.07 | 0 | 0.01 | 0.23
| Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 22:00 | For: AllOtherDays | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 22:00
| 0.47 | 0.1 | 0.29 | 0.49 | 0.02 | 0.18 | 0.9 | Until: 07:00 | 0.74 | 0.28 | 0.9 | 0.87 | 0.35 | 0.83 | 0.21 | 0.01 | 0.03 | 0.07 | 0 | 0.01 | 0.27
| Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 24:00 | 0 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 24:00
| 0.74 | 0.27 | 0.86 | 0.67 | 0.07 | 0.59 | 0.5 | Until: 19:00 | 0.92 | 0.57 | 0.96 | 0.93 | 0.45 | 0.93 | 0.37 | 0.01 | 0.22 | 0.15 | 0.01 | 0.03 | 0.2
| Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | For: Saturdays | 1 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00
| 0.81 | 0.45 | 0.95 | 0.81 | 0.05 | 0.8 | Until: 08:00 | Until: 24:00 | 0.93 | 0.71 | 0.99 | 0.92 | 0.42 | 0.98 | 0.52 | 0.07 | 0.78 | 0.32 | 0 | 0.04
| Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | 0.15 | 0 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00
| 0.8 | 0.42 | 0.98 | 0.77 | 0.09 | 0.84 | Until: 11:00 |  | 0.93 | 0.84 | 0.99 | 0.92 | 0.5 | 0.99 | 0.57 | 0.1 | 0.86 | 0.43 | 0.01 | 0.24
| Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | 0.3 |  | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00
| 0.81 | 0.34 | 0.97 | 0.75 | 0.08 | 0.92 | Until: 18:00 |  | 0.94 | 0.67 | 0.99 | 0.92 | 0.52 | 0.99 | 0.53 | 0.09 | 0.8 | 0.42 | 0 | 0.47
| Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | 0.8 |  | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00
| 0.77 | 0.4 | 0.95 | 0.78 | 0.1 | 0.91 | Until: 22:00 |  | 0.92 | 0.8 | 0.99 | 0.91 | 0.54 | 0.99 | 0.55 | 0.12 | 0.69 | 0.39 | 0.01 | 0.32
| Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | 0.9 |  | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00
| 0.73 | 0.37 | 0.94 | 0.79 | 0.07 | 0.83 | Until: 24:00 |  | 0.87 | 0.69 | 0.99 | 0.91 | 0.37 | 0.99 | 0.49 | 0.07 | 0.71 | 0.38 | 0 | 0.25
| Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | 0.5 |  | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00
| 0.69 | 0.35 | 0.91 | 0.75 | 0.06 | 0.83 | For: Sundays |  | 0.86 | 0.68 | 0.99 | 0.9 | 0.37 | 0.99 | 0.46 | 0.09 | 0.66 | 0.42 | 0 | 0.28
| Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 08:00 |  | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00
| 0.57 | 0.25 | 0.66 | 0.68 | 0.04 | 0.67 | 0.15 |  | 0.79 | 0.48 | 0.97 | 0.9 | 0.4 | 0.97 | 0.34 | 0.05 | 0.28 | 0.34 | 0 | 0.17
| Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 11:00 |  | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00
| 0.47 | 0.15 | 0.43 | 0.61 | 0.09 | 0.35 | 0.3 |  | 0.7 | 0.36 | 0.89 | 0.85 | 0.59 | 0.99 | 0.27 | 0.02 | 0.06 | 0.12 | 0.01 | 0.04
| Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 18:00 |  | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00
| 0.38 | 0.09 | 0.13 | 0.49 | 0.05 | 0.23 | 0.7 |  | 0.64 | 0.31 | 0.57 | 0.82 | 0.71 | 0.86 | 0.17 | 0 | 0.02 | 0.1 | 0 | 0.03
| Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 22:00 |  | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00
| 0.36 | 0.12 | 0.08 | 0.42 | 0.04 | 0.13 | 0.6 |  | 0.62 | 0.3 | 0.37 | 0.77 | 0.48 | 0.64 | 0.13 | 0.01 | 0.01 | 0.07 | 0 | 0.03
| For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | Until: 24:00 |  | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays | For: AllOtherDays
| Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | 0.5 |  | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00 | Until: 05:00
| 0.34 | 0.03 | 0.04 | 0.38 | 0.02 | 0.1 |  |  | 0.57 | 0.25 | 0.16 | 0.68 | 0.23 | 0.47 | 0.12 | 0 | 0 | 0.09 | 0 | 0.01
| Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 |  |  | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00 | Until: 06:00
| 0.34 | 0.03 | 0.04 | 0.38 | 0 | 0.06 |  |  | 0.57 | 0.25 | 0.16 | 0.75 | 0.18 | 0.55 | 0.13 | 0 | 0 | 0.09 | 0 | 0.01
| Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 |  |  | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00 | Until: 07:00
| 0.34 | 0.06 | 0.04 | 0.41 | 0.01 | 0.07 |  |  | 0.55 | 0.27 | 0.19 | 0.74 | 0.31 | 0.62 | 0.12 | 0 | 0 | 0.1 | 0 | 0.01
| Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 |  |  | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00 | Until: 08:00
| 0.34 | 0.02 | 0.05 | 0.42 | 0 | 0.11 |  |  | 0.6 | 0.33 | 0.21 | 0.79 | 0.25 | 0.58 | 0.15 | 0 | 0 | 0.1 | 0 | 0.01
| Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 |  |  | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00 | Until: 09:00
| 0.33 | 0.05 | 0.06 | 0.47 | 0.01 | 0.26 |  |  | 0.64 | 0.23 | 0.23 | 0.86 | 0.32 | 0.78 | 0.16 | 0 | 0 | 0.1 | 0 | 0.02
| Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 |  |  | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00 | Until: 10:00
| 0.36 | 0.12 | 0.07 | 0.54 | 0.03 | 0.43 |  |  | 0.65 | 0.42 | 0.35 | 0.87 | 0.49 | 0.9 | 0.21 | 0 | 0 | 0.12 | 0 | 0.03
| Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 |  |  | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00 | Until: 12:00
| 0.39 | 0.06 | 0.11 | 0.6 | 0.05 | 0.56 |  |  | 0.65 | 0.39 | 0.46 | 0.88 | 0.43 | 0.93 | 0.24 | 0 | 0 | 0.14 | 0 | 0.04
| Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 |  |  | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00 | Until: 13:00
| 0.38 | 0.05 | 0.1 | 0.65 | 0.02 | 0.54 |  |  | 0.64 | 0.46 | 0.47 | 0.88 | 0.42 | 0.91 | 0.26 | 0 | 0 | 0.23 | 0 | 0.03
| Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 |  |  | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00 | Until: 15:00
| 0.42 | 0.13 | 0.09 | 0.63 | 0.04 | 0.47 |  |  | 0.64 | 0.49 | 0.42 | 0.87 | 0.41 | 0.93 | 0.21 | 0 | 0 | 0.12 | 0 | 0.03
| Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 |  |  | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00 | Until: 16:00
| 0.38 | 0.11 | 0.08 | 0.6 | 0.06 | 0.41 |  |  | 0.63 | 0.35 | 0.38 | 0.86 | 0.41 | 0.94 | 0.18 | 0 | 0 | 0.08 | 0 | 0.02
| Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 |  |  | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00 | Until: 17:00
| 0.37 | 0.09 | 0.08 | 0.62 | 0.05 | 0.26 |  |  | 0.63 | 0.45 | 0.33 | 0.87 | 0.46 | 0.95 | 0.16 | 0.02 | 0 | 0.09 | 0 | 0.02
| Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 |  |  | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00 | Until: 18:00
| 0.37 | 0.13 | 0.09 | 0.59 | 0.04 | 0.25 |  |  | 0.61 | 0.41 | 0.34 | 0.84 | 0.38 | 0.97 | 0.15 | 0 | 0 | 0.1 | 0 | 0.02
| Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 |  |  | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00 | Until: 20:00
| 0.35 | 0.06 | 0.08 | 0.56 | 0.05 | 0.27 |  |  | 0.59 | 0.26 | 0.35 | 0.83 | 0.46 | 0.95 | 0.15 | 0 | 0 | 0.1 | 0 | 0.02
| Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 |  |  | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00 | Until: 22:00
| 0.33 | 0.05 | 0.07 | 0.45 | 0.02 | 0.15 |  |  | 0.58 | 0.33 | 0.23 | 0.78 | 0.56 | 0.78 | 0.15 | 0 | 0 | 0.09 | 0 | 0.02
| Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 |  |  | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00 | Until: 24:00
| 0.33 | 0.04 | 0.05 | 0.39 | 0.02 | 0.11 |  |  | 0.6 | 0.25 | 0.19 | 0.73 | 0.46 | 0.62 | 0.12 | 0 | 0 | 0.07 | 0 | 0.02

## Internal heat gains
12/12/19 v0.3 |  | Module B6 Operational Energy - internal heat gains
| Table B6.03: PEOPLE HEAT GAIN MODELLING: Commercial/Retail | [6 empty] | Table B6.04: INTERIOR LIGHTING ENERGY & HEAT GAIN MODELLING: Commercial/Retail |  |  | Table B6.05: HEAT GAIN TYPE & FRACTION ASSUMPTION FOR ALL ZONE ACTIVITIES: Commercial/Retail |  | Table B6.06: ELECTRIC EQUIPMENT: HOT WATER ENERGY & HEAT GAIN: Commercial/Retail |  | Table B6.07: ELECTRIC EQUIPMENT CONSUMPTION: PLUG LOAD ENERGY & HEAT GAIN MODELLING: Commercial/Retail |  | Table B6.08: PEOPLE HEAT GAIN MODELLING: Residential |  | Table B6.09: INTERIOR LIGHTING ENERGY & HEAT GAIN MODELLING: Residential |  | Table B6.10: ELECTRIC EQUIPMENT CONSUMPTION: PLUG LOAD ENERGY & HEAT GAIN MODELLING: Residential |  | Table B6.11: HOT WATER HEAT GAIN (FOR SPACE HEATING & COOLING LOAD CALCULATION) MODELLING: Residential |  | Table B6.12: HOT WATER HEAT GAIN (FOR SPACE HEATING & COOLING LOAD CALCULATION) MODELLING: Residential
|  | People per Zone Floor Area (m2) *1 | W/person M/F Adjusted |  | % Sensible Heat that is |  | Reference | Building Activity | Watts per Area (W/m2) | ASHRAE: Watts per Area (W/m2) | Ref: *8 (US Department of Energy, 2013) page 363-364. |  | Building Activity | Watts per Area (W/m2) | Building Activity | Watts per Area (W/m2) | Building Activity | Watts per Person (W) | Building Activity | Watts per Area (W/m2) | Building Activity | Watts per Area (W/m2) | Building Activity | Watts (W) | Calculated using EECA Water heating systems tool. Outputs of the tool are expressed as a cost per year to heat. This was converted to units kWh per person per year based on $0.29 per kWh and the following hot water system assumptions: https://www.energywise.govt.nz/tools/water-heating/
[5 empty] | Radiant for Air Velocity of Interior Environments |  |  |  |  | Ref: *7 | Return Air Fraction | 0 | Office | 2-8 W/m2
|  |  | Sensible | Latent | Low (0.1< V) | High (0.3 < V) |  | Office Open Plan | 3-21 W/m2 | 10.5 W/m2 | Fraction Radiant | 0.72 |  | Typical = 3 W/m2 | Office | 4-24 W/m2 | Family | 115 | Living | 0.88 | All zones | 24.5 | Hot Water (Heat Gain Only) | 100 | Number of Occupants | Auckland (kWh/year) | Wellington (kWh/year) | Christchurch (kWh/year)
| Office | 0.1 | 70 | 45 | 60% | 27% | *2 |  | Typical = 11 W/m2 |  | Fraction Visible | 0.18 |  | Ref: *9 |  | Typical = 8 W/m2 | Sleeping Adults | 70 | Kitchen | 0.96 | Fraction Latent | 0.017 | Sensible Heat Gain Fraction | 1 | 1 | 1789.6552 | 1893.1034 | 2013.7931
[9 empty] | Ref: *5 |  | Fraction Convected | 0.1 | Restaurant | 41 W/m2 |  | Ref: *5 | Sleeping Children | 70 | Kitchen/Living | 1.28 | Fraction Radiant | 0.4235 | Notes: NZS 4218:2009 Table G1 - Default power densities of rinternal gains from occupant and plug loads. |  | 2 | 2606.8966 | 2793.1034 | 3000
| Restaurant | 0.9 | 80 | 80 | 58% | 38% | *2 | Restaurant (Cafeteria, Fast Food) | 8 – 13 W/m2 | 14.1 W/m2 | References: |  |  | Ref: *9 | Restaurant | 55 Cooking, 8 Refrigeration, 36 Other Loads = 99W/m2 total | Fraction Radiant | 0.6 | Bedrooms | 0.21 | Fraction Lost | 0.137 |  |  | 3 | 3427.5862 | 3693.1034 | 3986.2069
| Lobbies and foyers | 1 | 75 | 70 | 58% | 38% | *2 |  | Ref: *6, and *8 |  | Return Air Fraction: the fraction of the heat from lights that goes into the zone return air. |  | Corridor | 0 W/m2 |  | Ref: *9 | Sensible Heat Fraction | Autocalculated by EnergyPlus | Other | 0.52 | Fraction Convected | 1-(sum of above) |  |  | 4 | 4248.2759 | 4593.1034 | 4975.8621
| Retail | 0.3 | 75 | 55 | 58% | 38% | *2 | Corridor (Communal non-residential – Assembly) | 11 W/m2 | 7.1 W/m2 | Fraction Radiant: the fraction of heat from lights that goes into the zone as long-wave (thermal) radiation, e.g. the radiation absorbed by the inside surfaces of the zone. |  |  | User Assumption | Corridor | 0.0 W/m2 | Notes: Table 1 Representative Rates at Which Heat and Moisture Are Given Off by Human Beings in Different States of Activity Chapter 18 Non-residential Cooling And Heating Load Calculations 2009 ASHRAE Handbook—Fundamentals (SI) (American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE), 2009). |  | Return Air Fraction | 0.86 | Notes: Fractions for the different heat transfer gains/losses were calculated based on the 2014 Building America House Simulation Protocols and the accompanying New Construction - benchamrk and NCTH calculation spreadsheet. User assuption: 50/50 split of sensible heat gain into radiant and convected heat gains. |  |  |  | 5 | 5068.9655 | 5493.1034 | 5962.069
| Corridor | 0.3 | 75 | 70 | 58% | 38% | *2 |  | Ref: *6, and *8 |  |  |  | Retail | 4-24 W/m2 |  | User assumption – included in other activities |  |  | Fraction Radiant | 0.04 |  |  |  |  | Shower flow rate | 8
| Car Parking | 0.002 | 75 | 70 | 58% | 38% | *2 | Retail | 6-26 W/m2 | 18.1 W/m2 | Fraction Visible: the fraction of heat from lights that goes into the zone as visible (short-wave) radiation. |  |  | Typical = 7W/m2 | Retail | 3-58 W/m2 |  |  | Fraction Visible | 0.1 |  |  |  |  | Length of shower | 10
| Gym Fitness Areas | 0.2 | 210 | 315 | 54% | 19% High Air for Cooling | *2 |  | Typical = 14 W/m2 |  | Assumed all lighting is surface mounted |  |  | Ref: *5 |  | Typical = 15 W/m2 |  |  | Fraction Replaceable (daylight control, full dimming or no dimming) | No dimming |  |  |  |  | Number of showers per day | 1 per occupant
| Notes: | [7 empty] | Ref: *5 |  |  |  | Gym Fitness Areas | 0 W/m2 |  | Ref: *5 |  |  | Notes: Interior lighting power density was calculated from the BRANZ report EC1353 Accurate modification for New Zealand, which uses the BRANZ HEEP study as measured source material. The power densities are from the winter period, May - September, and the electricity consumed when lighting is at max e.g. all lighting in the respective zone is on. A schedule is then used to modify this power density per hourly timestep. The hourly lighting load variation between zones was fairly constant, maximum difference of 1.7% and an average of 1.0%. Therefore a single schedule modifying lighting power intensity was developed from an average of the hourly lighting load variation of all zones. | [5 empty] | Number of baths per day | 0
| *1 Table 4: Occupant Densities (adapted from C/AS1 Part 2) Acceptable Solution G1/AS1 Personal Hygiene (Department of Building and Housing, 2011). | [6 empty] | Car Parking | 4.0 W/m2 | 2.0 W/m2 |  |  | Car Parking | 0 W/m2 | Gym Fitness Areas | 15 W/m2 User Assumption | [8 empty] | Hot water cylinder capacity | 180L
| *2 Table 1 Representative Rates at Which Heat and Moisture Are Given Off by Human Beings in Different States of Activity Chapter 18 Non-residential Cooling And Heating Load Calculations 2009 ASHRAE Handbook—Fundamentals (SI) (American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE), 2009). | [7 empty] | Ref: *6, and *8 |  |  |  | Storage | 0 W/m2 | Car Parking | 0 W/m2 | [8 empty] | Hot water cylinder location | Indoors
[8 empty] | Storage |  | 6.8 W/m2 |  |  | Atrium | 0 W/m2 | Storage | 0 W/m2 | [8 empty] | Electricity tariff (cent/kWh) inc. GST. Prompt payment discounts exlcuded. | 29
[8 empty] | Gym Fitness Areas |  | 7.8 W/m2 |  |  | Heat Gain Type Assumption For All Zone Activities |  | Atrium | 0 W/m2
[8 empty] | Atriums |  | 0.3 W/m2 |  |  | (User Assumptions) |  | Heat Gain Type Assumption For All Zone Activities
[8 empty] | Notes: |  |  |  |  | Fraction Latent | 0% | Fraction Latent | 0%
[8 empty] | *5 Based on BRANZ BEES data (Isaacs et al., 2014) |  |  |  |  | Fraction Radiant | 0% |  | User Assumption
[8 empty] | *6 Table 1 Building Purpose Lighting Power Densities NZS4243 Part 2:2007 NZS4243 Part 2:2007 Clause 3.3.1 states, “Lighting power density requirements apply to general and area lighting. They do not apply to (g) Lighting in plant and service areas that is on only occasionally.” (Standards New Zealand, 2007b) |  |  |  |  | Fraction Lost | 0% | Fraction Radiant | 20%
[13 empty] | Fraction Convected | 100% Simulation default |  | User Assumption
[8 empty] | *7 Table 9.6.1 Lighting Power Densities Using the Space By Space Method (ASHRAE Standards Committee, 2010) |  |  |  |  | Notes: |  | Fraction Lost | 0%
[13 empty] | *5 Based on BRANZ BEES data (Isaacs et al., 2014) |  | Fraction Convected | 80%
[13 empty] | *9 (Bishop & Isaacs, 2012, p. 20) |  | Notes:
[13 empty] | NZS4243 C4.2 Internal gains from domestic hot water are not required to be modelled. |  | *5 Based on BRANZ BEES data (Isaacs et al., 2014)
*9 (Bishop & Isaacs, 2012, p. 20)

## Zone airflow & ventilation
Module B6 Operational Energy - zone airflow and ventilation
Table B6.13: ZONE INFILTRATION: WHOLE BUILDING AVERAGE |  |  | Table B6.14: ZONE VENTILATION: OUTDOOR AIR REQUIREMENTS |  | Table B6.15: HVAC SCHEDULE OF OPERATION |  | Table B6.16a: RESIDENTIAL ZONE INFILTRATION |  |  |  | Table B6.16b: RESIDENTIAL ZONE VENTILATION: OPENING MODULATION |  |  |  | Table B6.16c: RESIDENTIAL HYBRID VENTILATION: CONDITIONS FOR OPENING WINDOWS/DOORS
Reference | Air Flow Rate | Notes | Building Activity | Air Flow Rate | OfficeHVAC_HoursOfOperation | RetailHVAC_HoursOfOperation | Reference | Space | Air Flow Rate | Notes | Opening Properties | Window | Exterior Door | Interior Door | Outdoor Conditions | Setting
*1 BRANZ BEES templates | 0.1 ACH |  | Office | 0.01 L/s*m2 | Fraction | Fraction | *19 BRANZ ALF Manual | Main Building | 0.15 ACH @ 4Pa | Specifications in ALF. Building constructed 2005+. Simple envelope complexity | Discharge co-efficient for opening | 0.4 | 1 | 1 | Maximum Wind Speed | 5m/s
*10 CIBSE Environmental Design Guide A page 4-24 (m3*h-1/m2 at 50 Pa) (CIBSE, 2015) | 20 m3*h-1/m2 | An existing ‘leaky’ building that does not comply with current regulations |  | Ref: *11 | Through: 12/31 | Through: 12/31 | *18 Roof space ventilation in New Zealand houses | Roofspace | 1/300*Area of insulated ceiling | "The size of the ventilation is often described as a ratio between the net free opening area of the vents to the area of insulated ceiling. While ratios ranging from 1:150 to 1:600 can be found, 1:300 seems to be a frequently specified fraction." - *18 BRANZ (2018) | 0.4 discharge co-efficient based on awning window style to approximate the windows opening effectiveness. |  |  |  | Minimum outdoor temperature | 10oC
| 10 m3*h-1/m2 | A building compliant with 2002 Part L Building Regulations | Restaurant (Dining Room, Cafeteria, Fast Food) | 0.01 L/s*m2 | For: Weekdays | For: Weekdays |  |  |  |  | Opening Modulation Factor | 0.1 | 0.1 | 0.25 | Maximum outdoor temperature | 24.9oC
| 7 m3*h-1/m2 | A moderately ‘tight’ building compliant with 2005 Part L Building Regulations. |  | Ref: *11 | Until: 07:00 | Until: 09:00 |  |  |  |  | Indoor and Outdoor Temperature Difference | 1-15/30oC | 1-15/30oC | 1-100oC | Raining | Closed
| 5 m3*h-1/m2 | A ‘tight’ building likely to comply with the 2013 Part L Building Regulations to ensure compliance with CO2 emission targets | Corridors | 0.25 L/s*m2 | 0 | 0 |  |  |  |  | Notes:
| 3 m3*h-1/m2 | A very ‘tight’ building |  | Ref: *11 | Until: 20:00 | Until: 20:00 |  |  |  |  | 30oC upper limit for windows and exterior doors in heated zones. 15oC upper limit for windows and exterior doors in heated and cooled zones. Limit temperatures defined through building tuning/testing. Modelled using bulk airflow (multizone) without distribution. Wind pressure co-efficient automatically calculated using Surface Average Calculation method.
|  |  | Retail Basement & Street Level | 1.5 L/s*m2 | 1 | 1
|  |  |  | Ref: *11 | Until: 24:00 | Until: 24:00
|  |  | Retail Upper Floors | 1.0 L/s*m2 | 0 | 0
|  |  |  | Ref: *11 | For: AllOtherDays | For: AllOtherDays
|  |  | Car Parking | 7.5 L/s*m2 | Until: 24:00 | Until: 10:00
|  |  |  | Ref: *11 | 0 | 0
Reference: *1 BRANZ BEES templates
|  |  | Air Velocity m/s | 0.1 – 0.3 m/s
Ref: *12
Typical = 0.2 m/s
Schedule
Notes:
*11 Table 2 Outdoor Air Requirements For Ventilation NZS4303:1990 11 (Standards New Zealand, 1990)
*12 CIBSE air velocities. Still air 0.1m/s < v < 0.3m/s (Awbi, 2004)

## Thermostat setpoint and HVAC
Module B6 Operational Energy - thermostat setpoint and HVAC systems
Table B6.17a: THERMOSTAT SETPOINTS | Table B6.17b: TYPES OF HVAC SYSTEMS |  |  | Centralised HVAC systems |  | Table B6.17c: RESIDENTIAL HEAT PUMP SETTINGS
18-25oC | HVAC System Properties | Heat Pump | Fan Coil Unit | Variable Air Volume electric heat | Variable Air Volume | HVAC System Properties | Heat Pump
| Controls installed | Thermostat | Thermostat, BMS | Thermostat, BMS | Thermostat, CO2 Sensor, BMS | Control type | Load
| Outdoor air supply rate (L/s/person) | 10 | 10 | 10 | 15 | Supply fan placement | Draw through
| Cooling coil | DX | Water | Water | Water | Cooling coil | Single Speed DX
| Heating coil | DX | Water | Electric | Water | Heating coil | Single Speed DX
| Supply fan placement | Draw through | - | Draw through | Draw through | Supply fan efficiency | 0.7
| Fan layout | - |  | Parallel | Parallel | Supply fan motor efficiency | 0.9
| Supply fan operation | Cycling |  | - | - | Cooling COP | 2
| Preheat coil | - |  | Electric |  | Heating COP | 2
| Reheat coil |  |  | Electric | Water | Notes: Heat pump assumptions based on simualtion defaults and adapted where better New Zealand specific information was available based on measured heat pump performance is New Zealand homes BRANZ SR329:2015. COP range 1.5-3.0 reported in BRANZ SR329:2015. Modelled COP 2.0 as conservative assumption.
| Baseboard heating type |  |  | - | Water
| Heat recovery |  |  |  | Enthalpy
| Night cycle ventilation |  |  |  | Central air handler
| Chiller type |  | Centrifugal | Centrifugal | Centrifugal
| Chiller to coils loop pump type |  | Prim. Constant | Prim. Constant | Prim. Constant
|  |  | Sec. Variable | Sec. Variable | Sec. Variable
| Condenser type |  | Air cooled | Air cooled | Water cooled
| Condenser water temperature control |  | - | - | Variable, based on outside temperature
| Chiller to condenser water loop pump type |  |  |  | Variable
| Cooling tower type |  |  |  | Two speed
| Boiler fuel |  | Natural gas |  | Natural gas
| Boiler to coils loop pump type |  | Variable |  | Variable
| Supply fan efficiency | 0.7 | 0.7 | 0.7 | 0.7
| Supply fan motor efficiency | 0.9 | 0.9 | 0.9 | 0.9
| Cooling coil design set point (oC) |  | 14 | 15 | 15
| Heating coil design set point (oC) |  | 50 | 12 | 10
| Preheat coil design set point (oC) |  | - | 6 | -
| Heat recovery effectiveness - Sensible | - |  | - | 0.75
| Heat recovery effectiveness - Latent |  |  |  | 0.7
| Chiller COP |  | 2.5 | 3.8 | 4.2
| Chilled water set point (oC) |  | 6 | 7.2 | 6
| Condenser water design set point (oC) |  | - | - | 30
| Boiler efficiency |  | 0.85 |  | 0.9
| Hot water set point (oC) |  | 82 |  | 80
| Cooling COP | 4.2 | - |  | -
| Heating COP | 4
Reference: *13 (Gates, 2013)

## Building materials
Module B6 Operational Energy - building materials
Heading definitions in Table B6.13 and information are provided below Table B6.13. Glazing and glazing frame materials information is provided in the Glazing & frames worksheet.
Table B6.18: BUILDING MATERIALS | [8 empty] | Table B6.19: ROUGHNESS (ENERGYPLUS)
*10 (CIBSE, 2015, pp. 3–44, 3–45) | [8 empty] | Roughness index | Example material
*14 (American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE), 2009b) | [8 empty] | VeryRough | Stucco
*15 Table 3.2 page 11 http://www.expol.co.nz/pdfs/EXPOL_PRODUCT-tech_guide_2015.pdf | [8 empty] | Rough | Brick
*16 Table E1a-d - R-values of Building Materials (Standards New Zealand, 2006) | [8 empty] | MediumRough | Concrete
*D Default figure | [8 empty] | MediumSmooth | Clear pine
Note: A High emissivity E>0.8, Low Emissivisty ≤0.2. Radiation accounts for about two thirds of total heat transfer and most building materials have high emissivities (between 0.9 and 0.95). Low emissivity materials such as aluminium foil have a higher resistance to radiation heat transfer (CIBSE, 2015, pp. 3–6). | [8 empty] | Smooth | Smooth plaster
Material | Roughness (dimensionless) | Thickness (m) | Conductivity (W/m*K) | Density (kg/m3) | Specific Heat (J/kg*K) | Thermal Absorption = | Solar Absorption = | Visible Absorption = | VerySmooth | Glass
[6 empty] | thermal emissivity aka thermal emittance *A | 1.0 – (Solar reflectance aka reflectivity) | 1.0 – (Visible reflectance aka reflectivity) | Reference:
Concrete | MediumRough | Varies | 1.3 *16 | 2200 *16 | 800-1000 *14 | 0.85 - 0.95 *10 | 0.65 - 0.80 *10 | 0.5 *D Medium | *8 Table 6. Roughness Coefficients D, E, and F (US Department of Energy, 2014, p. 65).
Fibre Cement | MediumSmooth | Varies | 1470 *16 | 0.25 *16 | 840 *14 | 0.95-0.96 *10 | 0.61-0.83 *10 | 0.5 *D Medium
(Proxy: Asbestos cement)
Fibre reinforced bitumen | MediumSmooth | Varies | 0.43 *16 | 1600 *16 | 1000 *14 | 0.91 *10 | 0.86 – 0.89 *10 | 0.4 *D Dark
Gypsum Plasterboard | Smooth | Varies | 800 *16 | 0.22 *16 | 1150 *14 | 0.9 *D | 0.7 *D | 0.6 *D Light
Plywood | MediumSmooth | Varies | 550 *16 | 0.13 *16 | 1888 *14 | NA *10 | 0.82 – 0.94 *10 | 0.6 *D Light
(Proxy: Woods: beach, oak, etc.)
Profile Sheet Metal (Aluminium Dull/Rough Finish) | VerySmooth | Varies | 2800 *16 | 230 *16 | 420 *10 | 0.216 | 0.40 – 0.65 | 0.7 *D
[6 empty] | *10 (Aluminium surfaced roofing) | *10 (Aluminium Dull/Rough Finish)
Profile Sheet Metal (Aluminium Paint Finish) | VerySmooth | Varies | 2800 *16 | 230 *16 | 420 *10 | 0.27-0.67 *10 | 0.30-0.55 *10 | 0.7 *D
Profile Sheet Metal | VerySmooth | Varies | 7800 *16 | 50 *16 | 420 *10 | 0.95 *10 | 0.3 *10 | 0.7 *D
(Steel, Zinc Paint Finish)
Profile Sheet Metal | VerySmooth | Varies | 7800 *16 | 50 *16 | 480 *10 | 0.11-0.25 *10 | 0.05 *10 | 0.4 *D Light
(Steel, Zinc Oxidised)
Plaster | MediumRough | Varies | 1860 *16 | 0.8 *16 | 840 *14 | 0.91 *10 | 0.30-0.50 *10 | 0.5 *D Medium
Expanded Polystyrene (EPS) | Smooth | Varies | 0.037 *14 | 16 *14 | 1210 *14 | 0.9 *D | 0.7 *D | 0.7 *D
Varies depending on density 16kg/m3 – 28kg/m3: 0.037 W/m*K – 0.035 W/m*K
Extruded Polystyrene (XPS) | Smooth | Varies | 0.032 *15 | 30 *15 | 1210 *14 | 0.9 *D | 0.7 *D | 0.7 *D
Soil | Rough | Varies | 1500 *16 | 1.0 - 1.5 *16 | 840 *10 | 0.9 *D | 0.7 *D | 0.4
* D Dark surface default
Timber | MediumSmooth | Varies | 450 *16 | 0.12 *16 | 1680 *10 | 0.82 *10 (Proxy: Spruce) | 0.7 *D | 0.7 *D
Concrete Block Masonry - Infilled | MediumRough | Varies | 2200 *16 | 1.3 *16 | 800-1000 *14 | 0.94 *10 | 0.56-0.69 *10 | 0.5 *D Medium
Carpet | Rough | 10 *16 | 0.06 *16 | 320 *10 | R Value 0.17 | 0.89-0.92 *10 (Proxy: Fabric – unspecified) | 0.75 – 0.88 *10 (Proxy: wool, black) | 0.4 *D Dark
Low-Density Polythylene_3mm | VerySmooth | 3mm | 0.33 | 920 | 2100 | 0.27-0.67 *10 | 0.30-0.55 *10 | 0.4 *D Light
Brick | MediumSmooth | 0.07 | 1.2 | 1920 | 790 | 0.9 *D | 0.7 *D | 0.7 *D
Linoleum | Smooth | 0.003 | 0.22 | 1300 | 840 | 0.9 *D | 0.7 *D | 0.7 *D
Ceiling Tile (Mineral Fiber Board) | MediumSmooth | 0.1 | 0.1 | 0.1 | 1220 | 0.9 | 0.78 | 0.78
OSB | MediumSmooth | Varies | 0.13 | 700 | 1220 | 0.9 | 0.78 | 0.78
Particleboard | Rough | 0.02 | 0.14 | 700 | 1172 | 0.9 *D | 0.7 *D | 0.7 *D
Tile | Smooth | 0.015 | 0.8 | 1900 | 840 | 0.9 *D | 0.7 *D | 0.7 *D
EnergyPlus: Roughness | The relative roughness of a particular material layer. This parameter only influences the convection coefficients, more specifically the exterior convection coefficient. A special keyword is expected in this field with the options being “VeryRough”, “Rough”, “MediumRough”, “MediumSmooth”, “Smooth”, and “VerySmooth” in order of roughest to smoothest options” (US Department of Energy, 2013, p. 82). Table B6.14 above provides example materials.
EnergyPlus: Thickness | Thickness of the material layer in metres. This should be the dimension of the layer in the direction perpendicular to the main path of heat conduction. This value must be a positive. Modelling layers thinner (less) than 0.003 m (3mm) is not recommended. Instead, add those properties to one of the adjacent layers (US Department of Energy, 2013, pp. 82–83).
EnergyPlus: Conductivity | Units for this parameter are W/(m-K). Thermal conductivity must be greater than zero. Modelling layers with conductivity higher than 5.0 W/(m-K) is not recommended (US Department of Energy, 2013, p. 83).
EnergyPlus: Thermal Absorption – Long Wavelength Radiation | Fraction of incident long wavelength radiation that is absorbed by the material. This parameter is used when calculating the long wavelength radiant exchange between various surfaces and affects the surface heat balances (both inside and outside as appropriate). For long wavelength radiant exchange, thermal emissivity and thermal emittance are equal to thermal absorptance. Values for this field must be between 0.0 and 1.0 (with 1.0 representing “black body” conditions)” (US Department of Energy, 2013, p. 83). Refer Table 3.39-3.41 Absorptivity and emissivity tables (CIBSE, 2006, pp. 3–44, 3–45)
EnergyPlus: Solar Absorption – Short Wavelenth Radiation | Fraction of incident solar radiation that is absorbed by the material. Solar radiation includes the visible spectrum as well as infrared and ultraviolet wavelengths. This parameter is used when calculating the amount of incident solar radiation absorbed by various surfaces and affects the surface heat balances (both inside and outside as appropriate). If solar reflectance (or reflectivity) data is available, then absorptance is equal to 1.0 minus reflectance (for opaque materials). Values for this field must be between 0.0 and 1.0 (US Department of Energy, 2013, p. 83). Refer Table 3.39-3.41 Absorptivity and emissivity tables (CIBSE, 2006, pp. 3–44, 3–45).
NZS4243:2007 Part 1 C2.2.3 Walls for the reference building and proposed buildings shall have the same solar absorption. In the absence of specific documentation 0.7 should be used as a default.
NZS4243:2007 Part 1 C2.4.4 The roofs proposed and reference buildings shall have the same solar absorption (0.7 is an acceptable default).
The exterior roof surface shall be modelled using the aged solar reflectance and the1Ulal emittance determined in accordance with Section 5.5.3.1.1(a). Where aged test data is unavailable, the roof surface shall be modelled with a solar reflectance of 0.30 and a thermal emittance of 0.90 (ASHRAE Standards Committee, 2010, p. 93).
5.5.3.1.1: Roof Solar Reflectance and Thermal Emittance. Roofs, in climate zones 1 through 3 shall have one of the following:
(a) minimum three-year-aged solar reflectance of 0.55 when tested in accordance with ASTM C1549 or ASTM E191S, and in addition, a minimum three-year-aged thermal emittance of 0.75 when tested in accordance with ASTM C1371 or ASTM E408.
(b) a minimum three-year-aged Solar Reflectance Index of 64 when determined in accordance with the Solar Reflectance Index method in ASTM E19S0 using a convection coefficient of 2.1 Btu/h•ft2•oF (ASHRAE Standards Committee, 2010, p. 34).
EnergyPlus: Visible Absorption | Fraction of incident visible wavelength radiation that is absorbed by the material. Visible wavelength radiation is slightly different than solar radiation in that the visible band of wavelengths is much more narrow while solar radiation includes the visible spectrum as well as infrared and ultraviolet wavelengths. This parameter is used when calculating the amount of incident visible radiation absorbed by various surfaces and affects the surface heat balances (both inside and outside as appropriate) as well as the daylighting calculations. If visible reflectance (or reflectivity) data is available, then absorptance is equal to 1.0 minus reflectance (for opaque materials). Values for this field must be between 0.0 and 1.0 (US Department of Energy, 2013, p. 83).
C5.5 Surface reflectances for day lighting ca1culations shall be 80% for ceilings, 50% for walls, and 20% for floors (US Department of Energy, 2013, p. 146).
3.4.5: “Surface reflections of 0.7, 0.5 and 0.2 have been applied to ceiling cavity, walls and floor cavity respectively. Pg 13

## Air gaps
Module B6 Operational Energy - air gaps
Table B6.20a: AIR GAP SPACE - MATERIAL AIR GAP WITH EFFECTIVE EMITTANCE (E) OF 0.82 & TEMPERATURE DIFFERENCE OF 12ºC |  |  |  | Table B6.20b: AIR GAP SPACE - MATERIAL AIR GAP WITH EFFECTIVE EMITTANCE (E) OF 0.5 & TEMPERATURE DIFFERENCE OF 12ºC
Material | Vertical Air Gap/Space and Horizontal Direction of Heat Flow: | Horizontal Air Gap/Space and Upwards Direction of Heat Flow: | Horizontal Air Gap/Space and Upwards Direction of Heat Flow: | Material | Vertical Air Gap/Space and Horizontal Direction of Heat Flow: | Horizontal Air Gap/Space and Upwards Direction of Heat Flow: | Horizontal Air Gap/Space and Upwards Direction of Heat Flow:
| Wall Cavity | Roof Cavity | Subfloor Space |  | Wall Cavity | Roof Cavity | Subfloor Space
| Thermal Resistance (R m2K/W) |  |  |  | Thermal Resistance (R m2K/W)
Air Gap 13mm | 0.15 | 0.13 | 0.15 | Air Gap 13mm | 0.21 | 0.17 | 0.21
Air Gap 20mm | 0.16 | 0.13 | 0.17 | Air Gap 20mm | 0.23 | 0.18 | 0.24
Air Gap 40mm | 0.16 | 0.14 | 0.19 | Air Gap 40mm | 0.22 | 0.19 | 0.28
Air Gap 90mm | 0.16 | 0.15 | 0.2 | Air Gap 90mm | 0.22 | 0.2 | 0.31
Notes: |  |  |  | Notes:
Modelled in EnergyPlus as Material: Air Gap object, thermal resistance only as emittance effects taken into account using Table E3 NZS4214:2006. |  |  |  | Thermal resistance of air gaps is determined as Table E3 – Thermal Resistance for listed air space width and total emittance at mean cavity temperature of 18ºC as per NZS4214:2006.
Thermal resistance of air gaps is determined as Table E3 – Thermal Resistance for listed air space width and total emittance at mean cavity temperature of 18ºC as per NZS4214:2006. |  |  |  | Assumed temperature difference between cavity and outdoors 12ºC as per AS/NZS 4859.1:2002 K3.1 *17 (Standards New Zealand, 2002)
Assumed temperature difference between cavity and outdoors 12ºC as per AS/NZS 4859.1:2002 K3.1 |  |  |  | Effective emittance (E) of air gap/space is the emittance of all material surrounding the air gap/space 1/E = (1/e1 + 1/e2) -1
Effective emittance (E) of air gap/space is the emittance of all material surrounding the air gap/space 1/E = (1/e1 + 1/e2) -1 |  |  |  | Assumed emissivity of materials 0.67
Assumed high emissivity materials 0.9 as per CIBSE recommendations (CIBSE, 2015, pp. 3–6) |  |  |  | 1/E = 1 / [(1/0.67)+(1/0.67)-1] = Effective Emittance (E) is 0.5
1/E = (1/0.9)+(1/0.9)-1 = 1.22 E=1/1.22 = Effective Emittance (E) is 0.82 |  |  |  | Horizontal airspaces present a greater resistance to downward heat flow because downward convection is small. Also a small inclination e.g. less than 45º has only a minor effect on the convective heat transfer and therefore only a little effect on the thermal resistance of airspaces *10 (CIBSE, 2015, pp. 3–6).
Horizontal airspaces present a greater resistance to downward heat flow because downward convection is small. Also a small inclination e.g. less than 45º has only a minor effect on the convective heat transfer and therefore only a little effect on the thermal resistance of airspaces (CIBSE, 2015, pp. 3–6). |  |  |  | Assumed beyond 25-30mm air gap/space thermal resistance remains near constant *10, *16 (CIBSE, 2015, pp. 3–6; Standards New Zealand, 2006).
Assumed beyond 25-30mm air gap/space thermal resistance remains near constant *10 (CIBSE, 2015, pp. 3–6) *16 (Standards New Zealand, 2006).

## Glazing & frames
Module B6 Operational Energy - glazing and frame materials
Reference: Data source from LBNL Window 7 library | [5 empty] | Reference: Data source from LBNL Window 7 library | [7 empty] | Reference: Table C4 from NZS 4218:2009
Table 6.21: GLAZING MATERIALS | [5 empty] | Table 6.22: GLAZING FRAME MATERIALS | [7 empty] | Table 6.23: GLAZING FRAME MATERIALS - RESIDENTIAL
Name | ID_9801_3mm_OptafloatClear | ID_9804_4mm_OptafloatClear | ID_9804_6mm_OptafloatClear | ID_9804_9mm_OptafloatGrey | ID_9806_10mm_OptafloatClear | Typical Window Unit | Glazing | Frame Type | U-Value of Frame | Thermal Resistance (R-Value) of Frame m2K/W | U-Value of Total Window Unit | Thermal Resistance (R-Value) of Total Window Unit m2K/W | Solar Heat Gain Coefficient | Glazing | Frame Type | U-Value of Total Window Unit | Thermal Resistance (R-Value) of Total Window Unit m2K/W | Solar Heat Gain Coefficient | Visual Transmittance
Optical Data Type | SpectralAverage | SpectralAverage | SpectralAverage | SpectralAverage | SpectralAverage |  | 4mm Single Clear | Aluminium, no break | 12.7 | 0.078 | 5.5 | 0.18 | 0.774 | 4mm Single Clear | Aluminium, no break | 6.7 | 0.15 | 0.84 | 0.746
Thickness | 0.003 | 0.004 | 0.006 | 0.009 | 0.009398 | 1989 WERS Report: Generic Window Systems to be used for typical windows. |  | Wood/PVC | 3.1 | 0.32 | 4.49 | 0.22 | 0.748 | 4mm Double Clear | Aluminium, no break | 3.9 | 0.26 | 0.74 | 0.671
Solar Transmittance at Normal Incidence | 0.876 | 0.864 | 0.774 | 0.255 | 0.698 | Typical window is 1800mm unit width, 1500mm unit height, 2.7m2 area, and horizontal transom |  | Aluminium, thermally improved | 5.8 | 0.17 | 4.81 | 0.21 | 0.697 |  | Wood/PVC | 2.81 | 0.36 | 0.74 | 0.671
Front Side Solar Reflectance at Normal Incidence | 0.078 | 0.077 | 0.072 | 0.046 | 0.066 |  | 5mm Single Tinted | Aluminium, no break | 12.7 | 0.078 | 5.41 | 0.18 | 0.495 | 4mm Double clear/Low E | Aluminium, no break | 3.28 | 0.31 | 0.69 | 0.617
Back Side Solar Reflectance at Normal Incidence | 0.078 | 0.077 | 0.072 | 0.046 | 0.066 |  |  | Wood/PVC | 3.1 | 0.32 | 4.41 | 0.23 | 0.479 | 4mm Double clear/argon | Wood/PVC | 2.67 | 0.37 | 0.74 | 0.636
Visible Transmittance at Normal Incidence | 0.907 | 0.904 | 0.883 | 0.276 | 0.861 |  |  | Aluminium, thermally improved | 5.8 | 0.17 | 4.72 | 0.21 | 0.446 |  | Aluminium, thermally improved | 3.14 | 0.32 | 0.74 | 0.636
Front Side Visible Reflectance at Normal Incidence | 0.082 | 0.082 | 0.081 | 0.047 | 0.08 |  | 6mm Single Reflective | Aluminium, no break | 12.7 | 0.078 | 5.14 | 0.19 | 0.36 | 4mm Double clear/argon/Low | Aluminium, no break | 3.14 | 0.32 | 0.7 | 0.617
Back Side Visible Reflectance at Normal Incidence | 0.082 | 0.082 | 0.081 | 0.047 | 0.08 |  |  | Wood/PVC | 3.1 | 0.32 | 4.14 | 0.24 | 0.348 |  | Wood/PVC | 1.99 | 0.5 | 0.7 | 0.617
Infrared Transmittance at Normal Incidence | 0 | 0 | 0 | 0 | 0 |  |  | Aluminium, thermally improved | 5.8 | 0.17 | 4.45 | 0.22 | 0.324
Front Side Infrared Hemispherical Emissivity | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 |  | 4mm Double Clear | Aluminium, no break | 12.7 | 0.078 | 3.97 | 0.25 | 0.657
Back Side Infrared Hemispherical Emissivity | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 |  |  | Wood/PVC | 3.1 | 0.32 | 3.01 | 0.33 | 0.635
Conductivity | 1 | 1 | 1 | 1 | 1 |  |  | Aluminium, thermally improved | 5.8 | 0.17 | 3.28 | 0.3 | 0.591
Dirt Correction Factor for Solar and Visible Transmittance | 1 | 1 | 1 | 1 | 1 |  | 4mm Double clear/Low E | Aluminium, no break | 12.7 | 0.078 | 3.34 | 0.3 | 0.621
Solar Diffusing | No | No | No | No | No |  |  | Wood/PVC | 3.1 | 0.32 | 2.4 | 0.42 | 0.6
Young’s modulus | [7 empty] | Aluminium, thermally improved | 5.8 | 0.17 | 2.65 | 0.38 | 0.559
Poisson’s ratio | [6 empty] | 4mm Double tint/Low E | Aluminium, no break | 12.7 | 0.078 | 3.25 | 0.31 | 0.324
[8 empty] | Wood/PVC | 3.1 | 0.32 | 2.32 | 0.43 | 0.313
[8 empty] | Aluminium, thermally improved | 5.8 | 0.17 | 2.56 | 0.39 | 0.292

## References
Module B6 Operational Energy - references
1 | BRANZ BEES templates http://www.branz.co.nz/cms_display.php?sn=158&st=1&pg=9697
2 | Standards New Zealand. (2007a). NZS 4243: Part 1: 2007 New Zealand Standard Energy Efficiency - Large Buildings Part 1: Building Thermal Envelope. Standards New Zealand.
3 | Department of Building and Housing. (2011, October 10). Compliance Document for New Zealand Building Code: Clause G1 Personal Hygiene – Second Edition. Department of Building and Housing. Retrieved from https://www.building.govt.nz/building-code-compliance/g-services-and-facilities/g1-personal-hygiene/
4 | American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE). (2009). Chapter 18 Non-residential Cooling And Heating Load Calculations. In 2009 ASHRAE Handbook—Fundamentals (SI). ASHRAE.
5 | Isaacs, N., Saville-Smith, K., Donn, M., Pollard, A., Babylon, M., Bishop, R., … Cory, S. (2014). Building Energy End-use Study (BEES) Part 2: Appendices To Final Report (Building Energy End-use Study (BEES) No. BRANZ Study Report 297/2). Judgeford, New Zealand: BRANZ.
6 | Standards New Zealand. (2007b). NZS 4243: Part 2: 2007 New Zealand Standard Energy Efficiency - Large Buildings Part 2: Lighting. Standards New Zealand.
7 | ASHRAE Standards Committee. (2010). ASHRAE Standard 90.1-2010: Energy Standard for Buildings Except Low-Rise Residential Buildings. American Society of Heating, Refrigerating and Air-Conditioning Engineers.
8 | US Department of Energy. (2013). EnergyPlus Input Output Reference: The Encyclopedic Reference to EnergyPlus Input and Output. US Department of Energy.
9 | Bishop, R., & Isaacs, N. (2012). Building Energy End-use Study (BEES) Year 5: Energy use outliers (No. SR277/3). Wellington New Zealand: BRANZ. Retrieved from http://www.branz.co.nz/cms_show_download.php?id=18e079430fb7917f536ee7488b865d7ababceab4
10 | CIBSE. (2015). CIBSE Guide A: Environmental Design (8th Edition). England: Chartered Institution of Building Services Engineers (CIBSE).
11 | Standards New Zealand. (1990). NZS 4303:1990: Ventilation For Acceptable Indoor Air Quality.
12 | Awbi, H. B. (2004). Ventilation Of Buildings (Second Edition). Routledge.
13 | Gates, A. (2013). Determining the Modelling Input Parameters for Heating, Ventilation, and Air Conditioning Systems in New Zealand Commercial Buildings (Master’s Thesis). Victoria Univeristy of Wellington, Wellington New Zealand.
14 | American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE). (2009b). Chapter 26 Heat, Air, and moisture Control in Building Assemblies - Material Properties. In 2009 ASHRAE Handbook—Fundamentals (SI). ASHRAE.
15 | Table 3.2 page 11 http://www.expol.co.nz/pdfs/EXPOL_PRODUCT-tech_guide_2015.pdf
16 | Standards New Zealand. (2006). NZS 4214:2006 Methods of Determining the Total Thermal Resistance of Parts of Buildings. Standards New Zealand.
17 | Standards New Zealand. (2002). Materials for the thermal insulation of buildings. Part 1: General criteria and technical provisions. Standards New Zealand.
18 | BRANZ. (2018). Roof space ventilation in New Zealand houses. In BRANZ Facts: Roof Ventilation #1. BRANZ. Retrieved from https://www.branz.co.nz/cms_show_download.php?id=70898781fd2e42476f813db50a122245d20cff6e
19 | BRANZ ALF Manual - Ventilation. Retrieved from https://alf.branz.co.nz/manual/understanding-alf-calculations/ventilation/